Installation cable S/FTP 4x2xAWG23/1, C.7, LSHF - E

Installation cable S/FTP 4x2xAWG23/1, for EN 50173 and ISO/IEC 11802 class F links or higher;

meets the specifications of EN 50288-4-1;

double cable jacket;

resistant against IRM 902, 903 according to IEC 60811-2-1 up to 7 days and 100 °C.

Rip cord between the two cable jackets;

reaction to fire class Eca or better according to European CPR;

fire retardant according to ISO/IEC 60332-3-24;

segregation classification “d” of EN 50174-2:2018-10;

Fire load: ≤ 0.185 kWh/m;

Cable outer diameter: ≤ 9.6 mm;

Colour of cable jacket: graphite grey like RAL 7024;

Manufacturer: Telegärtner

Type: TOC 900

Part No.: L02002A0175