Installation cable AMJ1300d S/FTP 23/1, Cat.7A, D-121

Installation cable S/FTP 2x(4x2xAWG23/1), for EN 50173 and ISO/IEC 11802 class FA links or higher;

RL ≥ 21 dB @ 1 GHz,

RL ≥ 18 dB @ 1.3 GHz,

to ensure high wire eccentricity;

meets the specifications of EN 50288-9-1;

cable jacket made of halogen-free, flame retardant material;

reaction to fire class Dca-s1,d2,a1 or better according to European CPR;

reaction to fire has to be printed on the cable jacket;

fire retardant according to ISO/IEC 60332-1;

segregation classification “d” of EN 50174-2:2018-10;

Fire load: ≤ 0.28 kWh/m;

Cable outer diameter: ≤ 7.5 x 16.5 mm;

Colour of cable jacket: blue;

Manufacturer: Telegärtner

Type: AMJ 1300

Part No.: L02002A0185